TEST PROCEDURE FOR HI-POT TESTING OF MULTI BOTTLE MONORUPTR VACUUM SWITCHES

- Test Equipment Required:

  - AC High pot machine capable of 50 kV peak or 36 kV  rms.

  - All recommended safety equipment per Hi-pot testing machine manufacturer.

- Test Setup:

- Place the vacuum Interrupter in an open area with suitable electrical clearances.

- Wipe the outside of all fiberglass tubes with denatured alcohol and a clean cloth.

- Prop Interrupter arms in the open position using a 6 ¾” long block of wood per photograph 1.  While opening the arms care must be taken to ensure that the arms are opened past the point where a “click” may be heard.  This “click” occurs when the internal contacts spring into the open position.

Photograph 1

- Verify that the contacts have opened by checking the continuity between the top and bottom aluminum flange of all Vacuum bottle modules to be tested.  See photograph 2.

Photograph 2

- Test Procedure:

- Starting from one end of the Vacuum Interrupter connect the high voltage test set lead to the upper flange of a module and the ground lead to the flange directly below.  These are the same points checked for continuity earlier.

- Gradually increase the voltage to 50 kV peak or 36 kV rms.

- Hold at this voltage for one minute.

- Vacuum bottle module should not Breakdown.

- If module does not breakdown continue with the next module until all modules have been tested.

- Test Results:

- A Defective Vacuum Interrupter will breakdown on one or more modules at a voltage well below 36 kV.

- A properly functioning Vacuum Interrupter will hold Voltage on all modules.

# Text boxes

Vacuum Bottle module

Vacuum Bottle module

Vacuum Bottle module

Vacuum Bottle module

Vacuum Bottle module

6 ¾” Block of wood

Test meter leads